## Component layout
Layout for E50 cabinet with S7-1500 and drive in main cabinet
| Maarten L 6-4-2023 V1.0 | Bridge | Bridge | Mark
301-2006 (900mm) | Kabelgoot 60 x 60 Verticaal links
758-9282 (160mm) | Kabelgoot 40 x 60 Verticaal rechts
758-9282 (450mm) | Kabelgoot 40 x 60 Horizontaal bovenste
758-9282 (450mm) | Kabelgoot 40 x 60 Horizontaal 2de van boven
758-9282 (450mm) | Kabelgoot 40 x 60 Horizontaal 3de van boven
758-9282 (250mm) | Kabelgoot 40 x 60 Horizontaal 4de van boven
758-9282 (250mm) | Kabelgoot 40 x 60 Horizontaal 5de van boven
742-4138 Din rail 430mm | Top din rail order from left to right
249-116 | Wago dinrail eindstop
6EP1433-2BA20 | SITOP PSU300S 24 V/5 A stabilized power supply |  |  | G1
6EP1961-2BA31 | SITOP PSE200U 3A 4-channel input: DC 24 V/12A |  |  | G2
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 | 2002-402 (2P) |  | X3.1
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X3.2
2002-1492 | eindkap terminal 2002-14XX (1 laags)
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 | 2002-402 (2P) |  | X3.3
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X3.4
2002-1492 | eindkap terminal 2002-14XX (1 laags)
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 | 2002-402 (2P) |  | X3.5
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X3.6
2002-1492 | eindkap terminal 2002-14XX (1 laags)
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 | 2002-402 (2P) |  | X3.7
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X3.8
2002-1492 | eindkap terminal 2002-14XX (1 laags)
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 | 2002-404 (4P) |  | X4.1
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X4.2
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X4.3
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  | 2002-404 (4P) | X4.4
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X4.5
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X4.6
2002-1401 | Wago term. grijs ¦ 1 etage, 4 draads klem ¦ 2.5mm2 |  |  | X4.7
2002-1492 | eindkap terminal 2002-14XX (1 laags)
1135752 | Elektroni beveiligingsschakelaar - (ralph) |  |  | Q10
249-116 | Wago dinrail eindstop
6ES7590-1AB60-0AA0 | Special din rail for S7-1500 PLC 160mm length | Bridge | Bridge | Mark
249-116 | Wago dinrail eindstop
6ES7511-1AK02-0AB0 | SIMATIC S7-1500, CPU 1511-1PN, 150KB Program, 1MB Data |  |  | N1
6ES7522-1BH01-0AB0 | SIMATIC S7-1500, DQ 16x24V DC/0.5A HF |  |  | N4
6ES7521-1BH10-0AA0 | SIMATIC S7-1500, DI 16x24VDC BA |  |  | N5
249-116 | Wago dinrail eindstop
742-4138 Din rail 430mm | 2nd din rail order from left to right
249-116 | Wago dinrail eindstop
3RV2021-4EA10 | zekering 27-32A voor heaters |  |  | Q5
3RV2021-1GA15 | Zekering voor transport pomp |  |  | Q6 | SET TO 5A!
5SY4103-7 | zekering 3A voor waterpomp & fans |  |  | Q8
5SY4102-7 | zekering 2A trilmotor |  |  | Q7
5SY4106-7 | zekering voor de voeding 24V |  |  | Q4
5SY7463-7 | hoofd zekering hele kast |  |  | Q3
249-116 | Wago dinrail eindstop
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 | 2010-403 (3P) |  | X2.1
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.2
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.3
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 | 2010-403 (3P) |  | X2.4
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.5
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.6
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 | 2010-402 (2P) |  | X2.7
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.8
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1204 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 | 2010-403 (3P) |  | X2.9
2010-1204 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.10
2010-1204 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X2.11
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1307 | Wago term. aarde ¦ 1 etage, 3 draads klem ¦ 10mm2 |  |  | X2.12
2010-1307 | Wago term. aarde ¦ 1 etage, 3 draads klem ¦ 10mm2 |  |  | X2.13
2010-1307 | Wago term. aarde ¦ 1 etage, 3 draads klem ¦ 10mm2 |  |  | X2.14
2010-1392 | Eindkap terminal 2010-13XX (1 laags)
249-116 | Wago dinrail eindstop
742-4138 Din rail 250mm | 3rd din rail order from left to right
249-116 | Wago dinrail eindstop
3RT2025-1BB40 | contactor voor alle heaters 7,5Kw |  |  | K5
3RT2016-1BB41 | Power contactor 4Kw transport pomp |  |  | K6
111-3042 | Single phase relais vibra motor |  |  | K7
111-3042 | Single phase relais water pump |  |  | K8
3RV2021-4EA10 | S0 servo motor protector, 27-32A |  |  | Q9
5SY4306-7 | zekering 3A voor waterpomp |  |  | Q4
2900376 | Solid State Relais Ralph |  |  | K10
249-116 | Wago dinrail eindstop
,k
742-4138 Din rail 250mm | 4rd din rail order from left to right
249-116 | Wago dinrail eindstop
3RF2330-1AA02 | Contactor 1 fase 3RF2 AC 51 / 30 A Zone 1 |  |  | K1
3RF2330-1AA02 | Contactor 1 fase 3RF2 AC 51 / 30 A Zone 2 |  |  | K2
3RF2330-1AA02 | Contactor 1 fase 3RF2 AC 51 / 30 A Zone 3 |  |  | K3
3RF2330-1AA02 | Contactor 1 fase 3RF2 AC 51 / 30 A Zone 4 |  |  | K4
3RF2330-1AA02 | Contactor 1 fase 3RF2 AC 51 / 30 A Zone 5 (nozzle) |  |  | K9
249-116 | Wago dinrail eindstop
742-4138 Din rail 250mm | 5th din rail order from left to right
249-116 | Wago dinrail eindstop
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X6.1
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X6.2
2010-1201 | Wago term. grijs ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X6.3
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 10mm2 |  |  | X6.4
2010-1292 | Eindkap terminal 2010-12XX (1 laags)
2010-1307 | Wago term. aarde ¦ 1 etage, 3 draads klem ¦ 10mm2 |  |  | X6.5
2010-1392 | Eindkap terminal 2010-13XX (1 laags)
2002-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 2.5mm2 | 2010-403 (3P) |  | X21.1
2002-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 2.5mm2 |  |  | X21.2
2002-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 2.5mm2 |  | 2010-403 (3P) | X21.3
2002-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 2.5mm2 |  |  | X21.4
2002-1204 | Wago term. blauw ¦ 1 etage, 2 draads klem ¦ 2.5mm2 |  |  | X21.5
2002-1292 | Eindkap terminal 2002-12XX (1 laags)
249-116 | Wago dinrail eindstop
111600 | TERZ Ethernet Switch 8p NITE-RF8-1100 |  |  | Q1
249-116 | Wago dinrail eindstop
Additional components mounted to the electrical plate
6SL3203-0CE23-8AA0 | Line reactor for S120 drives 50 series |  |  | T1
6SL3210-1PE23-8AL0 | S120 drive for 50 series |  |  | D1
6SL3040-1LA01-0AA0 | Control unit S120 drives |  |  | N6
Side panel 1 | P07-76925
CQF12 + CK 03 IAN | female 12 pin connector + haakse behuizing |  |  | X600
CQF03 + CK 03 IAN | female 3 pin connector + haakse behuizing |  |  | X601
CQF05 + CK 03 IAN | female 5 pin connector + haakse behuizing |  |  | X602
52015720 | PG11 wartel |  |  | X610
E12408 | m12 panel mount stekker |  |  | X620
E12408 | m12 panel mount stekker |  |  | X621
E12408 | m12 panel mount stekker |  |  | X622
798-0704 | ethernet panel mount |  |  | X630
798-0704 | ethernet panel mount |  |  | X631
Side panel 2 | P07-18499
52115750 | PG21 wartel for incoming power cable |  |  | X700
2x IE100050 | 2x 25 pin female connector for extruder heaters |  |  | X710
1437779 | Profibus panel mount |  |  | X720
6SL3066-2DA00-0AA0 | Coupler for servo encoder cable |  |  | X730
6FX2003-7BX00 | Servo power cable |  |  | X731
RJ45 panel mount #1 | Ethernet side panel |  |  | X740
RJ45 panel mount #2 | Ethernet side panel |  |  | X741
RJ45 panel mount #3 | Ethernet side panel |  |  | X742
IE100189 + IE100195 | 16 pin female on panel + 16 pin male in contra stekker |  |  | X750
890-703 | Snap-in socket; 3-pole; Cod. A; 1,50 mm²; black (Female) |  |  | X760
Cabinet externals | P07-78943
285-507 | 24V DC cooling fan #1 (top side of the cabinet) |  |  | F1
SK 3237.200 | Ventilation rooster |  |  | n/a
285-507 | 24V DC cooling fan #2 (bottom front of the door) |  |  | F1
SK 3237.200 | Ventilation rooster |  |  | n/a
3LD2504-0TK51 | Main power switch 63A |  |  | Q2
3LD9200-5B | Aux switch, contact |  |  | Q2.1
Cabinet servo and signal cables
6FX8002-5CN06-1AB0 | servo power cable from drive to sidepanel X731
6FX8002-2DC00-1AB0 | Servo encoder cable from drive to sidepanel X730
Q2.1
Q2

## Cable list
E50 with S7-1500 CPU
ass nr | From Part | from Mark | From terminal | color | mm2 | to part | to mark | to terminal | Function | additional info | length | end 1 | end 2
1 | 2010-1201 | X6 | 1.1 | brown | 10 | Main power switch in panel door | Q2 | 1/L1 | 3 phase to main power switch |  | 2000 | f | f
2 | 2010-1201 | X6 | 2.1 | black | 10 | Main power switch in panel door | Q2 | 3/L2 | 3 phase to main power switch |  | 2000 | f | f
3 | 2010-1201 | X6 | 3.1 | grey | 10 | Main power switch in panel door | Q2 | 5/L3 | 3 phase to main power switch |  | 2000 | f | f
4 | 2010-1204 | X6 | 4.1 | blue | 10 | Main power switch in panel door | Q2 | N | Neutral to main power switch |  | 1100 | f | f
5 | 2010-1207 | X6 | 5.1 | ylw/grn | 10 | Ground | X2 | 14.1 | Ground to ground distribution terminal | Terminal PE from now on | 1100 | f | f
6 | Main power switch in panel door | Q2 | 2/T1 | brown | 10 | Main fuse | Q3 | 1 | Main fuse L1 |  | 1300 | f | f
7 | Main power switch in panel door | Q2 | 4/T2 | black | 10 | Main fuse | Q3 | 3 | Main fuse L2 |  | 1300 | f | f
8 | Main power switch in panel door | Q2 | 6/T3 | grey | 10 | Main fuse | Q3 | 5 | Main fuse L3 |  | 1300 | f | f
9 | Main power switch in panel door | Q2 | N | blue | 10 | Main fuse | Q3 | 7 | Main fuse neutral
10 | Main fuse | Q3 | 2 | brown | 10 | 2010-1201 | X2 | 1.2 | L1 to L1 distribution terminal | Terminal L1 from now on | 300 | f | f
11 | Main fuse | Q3 | 4 | black | 10 | 2010-1201 | X2 | 5.2 | L2 to L2 distribution terminal | Terminal L2 from now on | 300 | f | f
12 | Main fuse | Q3 | 6 | grey | 10 | 2010-1201 | X2 | 8.2 | L3 to L3 distribution terminal | Terminal L3 from now on | 300 | f | f
13 | Main fuse | Q3 | 8 | blue | 10 | 2010-1201 | X2 | 11.2 | Neutral to neutral distribution terminal | Terminal N from now on | 300 | f | f
14 | 2004-1401 | X2 | L1 | brown | 2.5 | 5SY4106-7 | Q4 | 1 | Fuse for DC converter |  | 1200? | f | f
15 | 5SY4106-7 | Q4 | 2 | brown | 2.5 | PSU300S | G1 | L1 | Fuse for DC converter |  | 800 | f | f
16 | 2004-1403 | X2 | N | blue | 2.5 | PSU300S | G1 | N | Neutral for DC converter |  | 1200? | f | f
17 | 2004-1407 | X2 | PE | ylw/grn | 2.5 | PSU300S | G1 | PE | Ground for DC converter |  | 1200? | f | f
18 | PSU300S | G1 | + | red | 0.75 | SITOP PSE200U | G2 | 24V+ | 24V to 4 channel distributer |  | 250 | f | f
19 | PSU300S | G1 | + | red | 0.75 | SITOP PSE200U | G2 | 24V+ | 24V to 4 channel distributer |  | 250 | f | f
20 | PSU300S | G1 | - | black | 0.75 | SITOP PSE200U | G2 | 0V | 0V to 4 channel distributer |  | 350 | f | f
21 | PSU300S | G1 | - | black | 0.75 | 2002-1201 | X4 | 1.1 | 0V to 0V distribution terminal |  | 350 | f | f
22 | 2002-1201 | X4 | 1.2 | black | 0.75 | SITOP PSE200U | G2 | 0V | 0V to 4 channel distributer |  | 300 | f | f
23 | SITOP PSE200U | G2 | 1 | red | 0.75 | 2002-1201 | X3 | 1.1 | 24V group 1 |  | 250 | f | f
24 | SITOP PSE200U | G2 | 2 | red | 0.75 | 2002-1201 | X3 | 3.1 | 24V group 2 |  | 250 | f | f
25 | SITOP PSE200U | G2 | 3 | red | 0.75 | 2002-1201 | X3 | 5.1 | 24V group 3 |  | 250 | f | f
26 | SITOP PSE200U | G2 | 4 | red | 0.75 | 2002-1201 | X3 | 7.1 | 24V group 4 |  | 250 | f | f
27 | 2010-1201 | X2 | L1 | brown | 6 | 3RV2021-4EA10 | Q5 | 1/L1 | Fuse for the heaters |  | 400 | f | f
28 | 2010-1201 | X2 | L2 | black | 6 | 3RV2021-4EA10 | Q5 | 3/L2 | Fuse for the heaters |  | 400 | f | f
29 | 2010-1201 | X2 | L3 | grey | 6 | 3RV2021-4EA10 | Q5 | 5/L3 | Fuse for the heaters |  | 400 | f | f
30 | 3RV2021-4EA10 | Q5 | 2/T1 | brown | 6 | 3RT2025-1BB40 | K5 | 1/L1 | Safety contactor heatzones |  | 200 | f | f
31 | 3RV2021-4EA10 | Q5 | 4/T2 | black | 6 | 3RT2025-1BB40 | K5 | 3/L2 | Safety contactor heatzones |  | 200 | f | f
32 | 3RV2021-4EA10 | Q5 | 6/T3 | grey | 6 | 3RT2025-1BB40 | K5 | 5/L3 | Safety contactor heatzones |  | 200 | f | f
33 | 3RT2025-1BB40 | K5 | 2/T1 | brown | 6 | 3RF2330-1AA02 | K1 | 1L | Contactor heatzone 1 |  | 250 | f | f
34 | 3RT2025-1BB40 | K5 | 4/T2 | black | 6 | 3RF2330-1AA02 | K2 | 1L | Contactor heatzone 2 |  | 250 | f | f
35 | 3RT2025-1BB40 | K5 | 4/T2 | black | 6 | 3RF2330-1AA02 | K9 | 1L | Contactor heatzone 4 |  | 500 | f | f
36 | 3RT2025-1BB40 | K5 | 6/T3 | grey | 6 | 3RF2330-1AA02 | K3 | 1L | Contactor heatzone 3 |  | 300 | f | f
37 | 3RT2025-1BB40 | K5 | 6/T3 | grey | 6 | 3RF2330-1AA02 | K4 | 1L | Contactor heatzone nozzle |  | 300 | f | f
38 | 2010-1201 | X2 | N | blue | 6 | 2010-1201 | X21 | 1.2 | Neutral to N distribution for contactors | Terminal N from now on | 1200 | f | f
39 | 2010-1201 | X2 | L1 | brown | 6 | 3RV2021-1GA15 | Q6 | 1/L1 | Fuse for the transport pump |  | 400 | f | f
40 | 2010-1201 | X2 | L2 | black | 6 | 3RV2021-1GA15 | Q6 | 3/L2 | Fuse for the transport pump |  | 400 | f | f
41 | 2010-1201 | X2 | L3 | grey | 6 | 3RV2021-1GA15 | Q6 | 5/L3 | Fuse for the transport pump |  | 400 | f | f
42 | 3RV2021-1GA15 | Q6 | 1/L1 | brown | 6 | 3RT2016-1BB41 | K6 | L1 | Safety contactor transport pump |  | 200 | f | f
43 | 3RV2021-1GA15 | Q6 | 3/L2 | black | 4 | 3RT2016-1BB41 | K6 | L2 | Safety contactor transport pump |  | 200 | f | f
44 | 3RV2021-1GA15 | Q6 | 5/L3 | grey | 4 | 3RT2016-1BB41 | K6 | L3 | Safety contactor transport pump |  | 200 | f | f
45 | 2010-1201 | X2 | L1 | brown | 0.75 | 5SY4102-7 | Q7 | 1 | Fuse for the vibration magnet |  | 750 | f | f
46 | 5SY4102-7 | Q7 | 2 | brown | 0.75 | Omron 111-3042 | K7 | 11 | Relay for the vibration magnet |  | 600 | f | f
47 | 2010-1201 | X2 | L3 | grey | 0.75 | 5SY4103-7 | Q8 | 1 | Fuse for the waterpump |  | 750 | f | f
48 | 5SY4103-7 | Q8 | 2 | grey | 0.75 | Omron 111-3042 | K8 | 11 | Relay for the waterpump |  | 600 | f | f
49 | 2002-1401 | X3 | 1.4 | red | 0.75 | 111600 | Q1 | 24V | 24V to the ethernet switch |  | 1300 | f | f
50 | 2002-1401 | X4 | 2.1 | black | 0.75 | 111600 | Q1 | 0V | 0V to the ethernet switch |  | 1400 | f | f
51 | 2010-1307 | X2 | PE | ylw/grn | 0.75 | 111600 | Q1 | GND | GND to the ethernet switch |  | 1300 | f | f
52 | 2010-1201 | X2 | L1 | brown | 6 | S0 servo motor protector | Q9 | 1/L1 | Power to servo motor protector |  | 300 | f | f
53 | 2010-1201 | X2 | L2 | black | 6 | S0 servo motor protector | Q9 | 3/L2 | Power to servo motor protector |  | 300 | f | f
54 | 2010-1201 | X2 | L3 | grey | 6 | S0 servo motor protector | Q9 | 5/L3 | Power to servo motor protector |  | 300 | f | f
55 | S0 servo motor protector | Q9 | 2/T1 | brown | 6 | Line reactor for S120 drive | T1 | 2L1 | Power to line reactor for S120 drive |  | 1100 | f | f
56 | S0 servo motor protector | Q9 | 4/T2 | black | 6 | Line reactor for S120 drive | T1 | 2L2 | Power to line reactor for S120 drive |  | 1100 | f | f
57 | S0 servo motor protector | Q9 | 6/T3 | grey | 6 | Line reactor for S120 drive | T1 | 2L3 | Power to line reactor for S120 drive |  | 1100 | f | f
58 | 2010-1307 | X6 | 5.2 | ylw/grn | 6 | Line reactor for S120 drives | T1 | PE | Earthing of line reactor |  | 800 | f | f
59 | Line reactor for S120 drives | T1 | 2L1 | brown | 6 | Servo Drive | D1 | L1 | Power for the servo drive |  | 1100 | f | f
60 | Line reactor for S120 drives | T1 | 2L2 | black | 6 | Servo Drive | D1 | L2 | Power for the servo drive |  | 1100 | f | f
61 | Line reactor for S120 drives | T1 | 2L3 | grey | 6 | Servo Drive | D1 | L3 | Power for the servo drive |  | 1100 | f | f
62 | 2010-1307 | X6 | 6.1 | ylw/grn | 6 | Servo Drive | D1 | PE | Earthing of servo drive |  | 500 | f | f
63 | Servo connection cable | X731 | U | black | 0.75 | Servo Drive | D1 | U | Servo power |  | n/a | f | f
64 | Servo connection cable | X731 | V | black | 0.75 | Servo Drive | D1 | V | Servo power |  | n/a | f | f
65 | Servo connection cable | X731 | W | black | 0.75 | Servo Drive | D1 | W | Servo power |  | n/a | f | f
66 | Servo connection cable | X731 | PE | ylw/grn | 0.75 | Servo Drive | D1 | PE | Servo earth |  | n/a | f | f
67 | Control unit drive | N6 | + | red | 0.75 | 2002-1401 | X3 | 3.3 | Control unit V+ |  | 1000 | f | f
68 | Control unit drive | N6 | M | black | 0.75 | 2002-1401 | X4 | 3.3 | Control unit V- |  | 1100 | f | f
69 | Control unit drive | N6 | X150 P2 | green | n/a | Servo control connector in side panel | X730 | n/a | Servo control connection |  | 0.5m | f | f
70 | SIMATIC S7-1500 | N1 | +24V | red | 0.75 | 2002-1401 | X3 | 2.2 | PLC V+ |  | 400 | f | f
71 | SIMATIC S7-1500 | N1 | 0V | black | 0.75 | 2002-1401 | X4 | 2.2 | PLC V- |  | 300 | f | f
72 | SIMATIC S7-1500 | N1 | X1 (profinet) | green | n/a | Ethernet switch | Q1 | X1 | Profinet port 1 |  | 1m | rj45 | rj45
73 | SIMATIC S7-1500 | N1 | X2 (profinet) | green | n/a | free |  |  | Profinet port 2 |  | n/a | n/a | n/a
74 | SIMATIC S7-1500 DQ 16x24V | N4 | 1 | purple | 0.75 | Contactor heaters | K5 | +A1 | Safety contactor heaters |  | 1100 | f | f
75 | SIMATIC S7-1500 DQ 16x24V | N4 | 2 | purple | 0.75 | Contactor heatzone 1 | K1 | +A1 | Contactor heatzone 1 |  | 1400 | f | f
76 | SIMATIC S7-1500 DQ 16x24V | N4 | 3 | purple | 0.75 | Contactor heatzone 2 | K2 | +A1 | Contactor heatzone 2 |  | 1400 | f | f
77 | SIMATIC S7-1500 DQ 16x24V | N4 | 4 | purple | 0.75 | Contactor heatzone 3 | K3 | +A1 | Contactor heatzone 3 |  | 1400 | f | f
78 | SIMATIC S7-1500 DQ 16x24V | N4 | 5 | purple | 0.75 | Contactor heatzone 4 | K4 | +A1 | Contactor heatzone 4 | E50 only | 1500 | f | f
79 | SIMATIC S7-1500 DQ 16x24V | N4 | 6 | n/a | n/a | free |  |  |  | G40/G50 versions only | 1500 | f | f
80 | SIMATIC S7-1500 DQ 16x24V | N4 | 7 | purple | 0.75 | Contactor heatzone nozzle | K9 | +A1 | Contactor heatzone nozzle |  | 1500 | f | f
81 | SIMATIC S7-1500 DQ 16x24V | N4 | 8 | purple | 0.75 | Omron 111-3042 | K7 | + | Vibration motor relay |  | 900 | f | f
82 | SIMATIC S7-1500 DQ 16x24V | N4 | 9 | red | 0.75 | 2002-1401 | X3 | 2.3 | Voeding PLC |  | 1000 | f | f
83 | SIMATIC S7-1500 DQ 16x24V | N4 | 10 | black | 0.75 | 2002-1401 | X4 | 2.3 | Voeding PLC |  | 1000 | f | f
84 | SIMATIC S7-1500 DQ 16x24V | N4 | 11 | purple | 0.75 | 3RT2016-1BB41 | K6 | +A1 | Transport pump contactor |  | 900 | f | f
85 | SIMATIC S7-1500 DQ 16x24V | N4 | 12 | purple | 0.75 | Omron 111-3042 | K8 | + | WaterCooling relay |  | 900 | f | f
86 | SIMATIC S7-1500 DQ 16x24V | N4 | 13 | black | 0.75 | 2900376 | A1 | black wire | Festo valve 1 |  | 1200-500 | s | f
87 | SIMATIC S7-1500 DQ 16x24V | N4 | 14 | white | 0.75 | IFM E12408 | X620 | white wire | Festo valve 2 |  | 1200-500 | s | f
88 | SIMATIC S7-1500 DQ 16x24V | N4 | 15 | black | 0.75 | IFM E12408 | X621 | black wire | Festo valve 3 |  | 1200-500 | s | f
89 | SIMATIC S7-1500 DQ 16x24V | N4 | 16 | purple | 0.75 | ILME CKF 03 | X600 | pin 1 | Buzzer |  | 900 | f | ilme
90 | SIMATIC S7-1500 DQ 16x24V | N4 | 17 | purple | 0.75 | ILME CKF 03 | X600 | pin 10 | Led reset button |  | 900 | f | ilme
91 | SIMATIC S7-1500 DQ 16x24V | N4 | 18 | purple | 0.75 | 2900376 | K10 | A1 | Relais Rotary Airlock Valve |  | tbd | f | f
92 | SIMATIC S7-1500 DQ 16x24V | N4 | 19 | red | 0.75 | 2002-1401 | X3 | 3.2 | Voeding PLC |  | 550 | f | f
93 | SIMATIC S7-1500 DQ 16x24V | N4 | 20 | black | 0.75 | 2002-1401 | X4 | 3.2 | Voeding PLC |  | 450 | f | f
94 | SIMATIC S7-1500 DI 16x24V | N5 | 1 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
95 | SIMATIC S7-1500 DI 16x24V | N5 | 2 | black | 0.75 | Emergency button | n/a | 22 | UI panel - Emergency button |  | tbd | n/a | f
96 | SIMATIC S7-1500 DI 16x24V | N5 | 3 | white | 0.75 | 3RV2021-1GA15 | Q6 | 14 | Transport pump signal |  | 700 | f | f
97 | SIMATIC S7-1500 DI 16x24V | N5 | 4 | white | 0.75 | 3RV2021-4EA10 | Q5 | 14 | Heater fuse signal |  | 700 | f | f
98 | SIMATIC S7-1500 DI 16x24V | N5 | 5 | white | 0.75 | IFM E12408 | X622 | white wire | Storage sensor |  | 1200-500 | f | s
99 | SIMATIC S7-1500 DI 16x24V | N5 | 6 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
100 | SIMATIC S7-1500 DI 16x24V | N5 | 7 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
101 | SIMATIC S7-1500 DI 16x24V | N5 | 8 | white | 0.75 | 12 pin sidepanel connector for ui panel | X600 | pin 9 | Reset button |  | 1000 | f | ilme
102 | SIMATIC S7-1500 DI 16x24V | N5 | 9 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
103 | SIMATIC S7-1500 DI 16x24V | N5 | 10 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
104 | SIMATIC S7-1500 DI 16x24V | N5 | 11 | white | 0.75 | S0 servo motor protector | Q9 | 14 | Servo drive fuse signal |  | 800 | f | f
105 | SIMATIC S7-1500 DI 16x24V | N5 | 12 | white | 0.75 | 3RT2016-1BB41 | K6 | 14 | Contactor transport pump signal |  | 1200 | f | f
106 | SIMATIC S7-1500 DI 16x24V | N5 | 13 | white | 0.75 | 3RT2025-1BB40 | K5 | 14 | Contactor heaters signal |  | 1200 | f | f
107 | SIMATIC S7-1500 DI 16x24V | N5 | 14 | black | 0.34 | IFM E12408 | X622 | black wire | Cooling Flow OK sensor |  | 1200-500 | f | s
108 | SIMATIC S7-1500 DI 16x24V | N5 | 15 | white | 0.75 | Aux switch main | Q2.1 | 12 | aux switch from main power switch |  | 1200 | f | f
109 | SIMATIC S7-1500 DI 16x24V | N5 | 16 | white | 0.75 | SITOP PSE200U | G2 | S | Status from sitop module |  | 1100 | f | f
110 | SIMATIC S7-1500 DI 16x24V | N5 | 17 | white | 0.75 | 2002-1401 | X35 | 1.4 | Fans signal |  | 500 | f | f
111 | SIMATIC S7-1500 DI 16x24V | N5 | 18 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
112 | SIMATIC S7-1500 DI 16x24V | N5 | 19 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
113 | SIMATIC S7-1500 DI 16x24V | N5 | 20 | black | 0.75 | 2002-1401 | X4 | 3.3 | 0V |  | 700 | f | f
114 | ILME CQF 12 | X600 | pin 2 | black | 0.75 | 2002-1401 | X4 | 5.4 | 0V |  | 800 | ilme | f
115 | ILME CQF 12 | X600 | pin 3 | black | 0.75 | 2010-1201 | X2 | L2 | L2 |  | 800 | ilme | f
116 | ILME CQF 12 | X600 | pin 4 | blue | 0.75 | 2010-1201 | X2 | N | Neutral |  | 800 | ilme | f
117 | ILME CQF 12 | X600 | pin 5 | red | 0.75 | 2002-1401 | X3 | 5.2 | 24V |  | 800 | ilme | f
118 | ILME CQF 12 | X600 | pin 6 | black | 0.75 | 2002-1401 | X4 | 6.2 | 0V |  | n/a | ilme | f
119 | ILME CQF 12 | X600 | pin 7 | ylw/grn | 0.75 | 2010-1307 | X2 | PE | GND |  | 500 | ilme | f
120 | ILME CQF 12 | X600 | pin 8 | red | 0.75 | 2002-1401 | X3 | 5.4 | 24V |  | 1000 | ilme | f
121 | ILME CQF 12 | X600 | pin 11 | black | 0.75 | 2002-1401 | X4 | 6.4 | 0V |  | n/a | ilme | f
122 | ILME CQF 12 | X600 | pin 12 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
123 | ILME CKF 03 | X601 | pin 1 | grey | 0.75 | Omron 111-3042 | K8 | 14 | Power waterpump |  | 1000 | ilme | f
124 | ILME CKF 03 | X601 | pin 2 | blue | 0.75 | 2010-1201 | X2 | N | Neutral waterpump |  | 700 | ilme | f
125 | ILME CKF 03 | X601 | pin 3 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
126 | ILME CKF 03 | X601 | PE | ylw/grn | 0.75 | 2010-1307 | X2 | PE | Ground waterpump |  | 800 | ilme | f
127 | ILME CQF 05 | X602 | pin 1 | brown | 0.75 | 3RT2016-1BB41 | K6 | T1 | Power to transport pump |  | 900 | ilme | f
128 | ILME CQF 05 | X602 | pin 2 | black | 0.75 | 3RT2016-1BB41 | K6 | T2 | Power to transport pump |  | 900 | ilme | f
129 | ILME CQF 05 | X602 | pin 3 | grey | 0.75 | 3RT2016-1BB41 | K6 | T3 | Power to transport pump |  | 900 | ilme | f
130 | ILME CQF 05 | X602 | PE | ylw/grn | 0.75 | 2010-1201 | X2 | PE | Ground to transport pump |  | 1000 | ilme | f
131 | Emergency button | X610 | 11 | white | 0.75 | 2002-1401 | X3 | 3.1 | 24V to emergency button |  | tbd | n/a | f
132 | Emergency button | X610 | 12 | blue | 0.75 | Aux early break on main power switch | Q2.1 | 13 | Emergency button to input signal |  | tbd | n/a | f
133 | Emergency button | X610 | 21 | brown | 0.75 | 2002-1401 | X3 | 3.4 | 24V to emergency button |  | tbd | n/a | f
134 | IFM E12408 | X620 | pin 1 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
135 | IFM E12408 | X620 | pin 3 | blue | 0.75 | 2002-1401 | X4 | 3.4 | 0V |  | 800 | f | f
136 | IFM E12408 | X620 | pin 5 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
137 | IFM E12408 | X621 | pin 1 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
138 | IFM E12408 | X621 | pin 2 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
139 | IFM E12408 | X621 | pin 3 | blue | 0.75 | 2002-1401 | X4 | 4.2 | 0V |  | 800 | f | f
140 | IFM E12408 | X621 | pin 5 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
141 | IFM E12408 | X622 | pin 1 | brown | 0.75 | 2002-1401 | X3 | 5.3 | 24V |  | 800 | f | f
142 | IFM E12408 | X622 | pin 2 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
143 | IFM E12408 | X622 | pin 3 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
144 | IFM E12408 | X622 | pin 5 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
| ILME CDF 25 (Y) | X710 | A1 | brown | 2.5 | 3RF2330-1AA02 | K1 | 2T | L heatzone 1 top |  | 600 | ilme | f
146 | ILME CDF 25 (Y) | X710 | A2 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 1 top |  | 600 | ilme | f
147 | ILME CDF 25 (Y) | X710 | A3 | brown | 2.5 | 3RF2330-1AA02 | K1 | 2T | L heatzone 1 bottom |  | 600 | ilme | f
148 | ILME CDF 25 (Y) | X710 | A4 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 1 bottom |  | 600 | ilme | f
149 | ILME CDF 25 (Y) | X710 | A5 | black | 2.5 | 3RF2330-1AA02 | K2 | 2T | L heatzone 2 top |  | 600 | ilme | f
150 | ILME CDF 25 (Y) | X710 | A6 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 2 top |  | 600 | ilme | f
151 | ILME CDF 25 (Y) | X710 | A7 | black | n/a | 3RF2330-1AA02 | K2 | 2T | L heatzone 2 bottom |  | n/a | n/a | n/a
152 | ILME CDF 25 (Y) | X710 | A8 | blue | n/a | 2010-1201 | X21 | N | N heatzone 2 bottom |  | n/a | n/a | n/a
153 | ILME CDF 25 (Y) | X710 | A9 | grey | 2.5 | 3RF2330-1AA02 | K3 | 2T | L heatzone 3 top |  | 600 | ilme | f
154 | ILME CDF 25 (Y) | X710 | B2 | blue | 2.5 | 2010-1201 | X21 | 2T | N heatzone 3 top |  | 600 | ilme | f
155 | ILME CDF 25 (Y) | X710 | B3 | grey | 2.5 | 3RF2330-1AA02 | K3 | 2T | L heatzone 3 bottom |  | 600 | ilme | f
156 | ILME CDF 25 (Y) | X710 | B4 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 3 bottom |  | 600 | ilme | f
157 | ILME CDF 25 (Y) | X710 | B5 | grey | 2.5 | 3RF2330-1AA02 | K4 | 2T | L heatzone 4 top |  | 600 | ilme | f
158 | ILME CDF 25 (Y) | X710 | B6 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 4 top |  | 600 | ilme | f
159 | ILME CDF 25 (Y) | X710 | B7 | grey | 2.5 | 3RF2330-1AA02 | K4 | 2T | L heatzone 4 bottom |  | 600 | ilme | f
160 | ILME CDF 25 (Y) | X710 | B8 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone 4 bottom |  | 600 | ilme | f
161 | ILME CDF 25 (Y) | X710 | C1 | black | 2.5 | 3RF2330-1AA02 | K9 | 2T | L heatzone nozzle |  | 600 | ilme | f
162 | ILME CDF 25 (Y) | X710 | C2 | blue | 2.5 | 2010-1201 | X21 | N | N heatzone nozzle |  | 600 | ilme | f
163 | ILME CDF 25 (Y) | X710 | C3 | red | 2.5 | 2002-1401 | X3 | 7.2 | ET200 - 24V |  | 1200 | ilme | f
164 | ILME CDF 25 (Y) | X710 | C4 | black | 2.5 | 2002-1401 | X4 | 3.2 | ET200 - 0V |  | 1200 | ilme | f
165 | ILME CDF 25 (Y) | X710 | C5 | red | 2.5 | 2002-1401 | X3 | 7.4 | ET200 - 24V geschakeld |  | 1200 | ilme | f
166 | ILME CDF 25 (Y) | X710 | C6 | black | 2.5 | 2002-1401 | X4 | 3.4 | ET200 - 0V |  | 1200 | ilme | f
167 | ILME CDF 25 (Y) | X710 | C7 | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
168 | ILME CDF 25 (Y) | X710 | C8 | brown | 2.5 | Omron 111-3042 | K7 | 14 | Vibration motor |  | 600 | ilme | f
169 | ILME CDF 25 (Y) | X710 | C9 | blue | 2.5 | 2010-1201 | X21 | N | Vibration motor |  | 600 | ilme | f
170 | ILME CDF 25 (Y) | X710 | PE | ylw/grn | 2.5 | 2010-1207 | X6 | 5.1 | Vibration motor ground |  | 600 | f | f
171 | ILME CDF 25 Z (X) | X710 | A1 - C9 + PE | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
172 | 3RV2021-4EA10 | Q5 | 13 | red | 0.75 | 3RV2021-1GA15 | Q6 | 13 | 24V to heater fuse |  | 200 | f | f
173 | 3RV2021-1GA15 | Q6 | 13 | red | 0.75 | 2002-1401 | X3 | 2.4 | 24V to transport pump fuse |  | 250 | f | f
174 | 3RT2025-1BB40 | K5 | 13 | red | 0.75 | 3RT2016-1BB41 | K6 | 13 | 24V to contactor transport pump |  | 200 | f | f
175 | 3RT2025-1BB40 | K5 | 13 | red | 0.75 | 2002-1401 | X3 | 2.3 | 24V to contactor heatzones |  | 900 | f | f
176 | S0 servo motor protector | Q9 | 13 | red | 0.75 | 2002-1401 | X3 | 1.3 | 24V to servo motor protector |  | 1200 | f | f
177 | 3RF2330-1AA02 | K1 | A2 | black | 0.75 | 2002-1401 | X4 | 3.3 | 0V to contactor heatzone 1 control |  | 1400 | f | f
178 | 3RF2330-1AA02 | K2 | A2 | black | 0.75 | 2002-1401 | X4 | 4.1 | 0V to contactor heatzone 1b control |  | 1400 | f | f
179 | 3RF2330-1AA02 | K3 | A2 | black | 0.75 | 2002-1401 | X4 | 4.3 | 0V to contactor heatzone 2 control |  | 1400 | f | f
180 | 3RF2330-1AA02 | K4 | A2 | black | 0.75 | 2002-1401 | X4 | 5.1 | 0V to contactor heatzone nozzle control |  | 1400 | f | f
181 | 3RT2025-1BB40 | K5 | 0V | black | 0.75 | 2002-1401 | X4 | 2.3 | 0V to safety contactor heatzones control |  | 1200 | f | f
182 | 3RT2016-1BB41 | K6 | 0V | black | 0.75 | 2002-1401 | X4 | 3.1 | 0V to contactor transport pump control |  | 1200 | f | f
183 | Omron 111-3042 | K7 | A2 | black | 0.75 | 2002-1401 | X4 | 4.4 | 0V to contactor vibration magnet control |  | 1400 | f | f
184 | Omron 111-3042 | K8 | A2 | black | 0.75 | 2002-1401 | X4 | 5.2 | 0V to contactor waterpump control |  | 1400 | f | f
185 | 3RF2330-1AA02 | K9 | A2 | black | 0.75 | 2002-1401 | X4 | 5.3 | 0V to contactor heatzone 3 |  | 1600 | f | f
186 | Top cooling fan (side panel) | C1 | n/a | red | 0.34 | 2002-1401 | X35 | 1.1 | +24V Cooling fan, make sure it is blowing outside |  | 600 | f | f
187 | Top cooling fan (side panel) | C1 | n/a | black | 0.34 | 2002-1401 | X4 | 6.3 | Gnd Cooling fan, make sure it is blowing outside |  | 500 | f | f
188 | Bottom cooling fan (door) | C2 | n/a | red | 0.34 | 2002-1401 | X35 | 1.2 | +24VCooling fan, make sure it is blowing inside |  | 600 | f | f
189 | Bottom cooling fan (door) | C2 | n/a | black | 0.34 | 2002-1401 | X4 | 5.4 | Gnd Cooling fan, make sure it is blowing inside |  | 500 | f | f
190 | Temperature controller | n/a | L | red | 0.75 | 2002-1401 | X3 | tbd | 24V Temperature controller |  | 800 | f | f
191 | CEE power plug | X700 | n/a | brown | 10 | 2010-1201 | X6 | 1.2 | 3 phase to main power terminal |  | n/a | f | f
192 | CEE power plug | X700 | n/a | black | 10 | 2010-1201 | X6 | 2.2 | 3 phase to main power terminal |  | n/a | f | f
193 | CEE power plug | X700 | n/a | grey | 10 | 2010-1201 | X6 | 3.2 | 3 phase to main power terminal |  | n/a | f | f
194 | CEE power plug | X700 | n/a | blue | 10 | 2010-1203 | X6 | 4.2 | Neutral to main neutral terminal |  | n/a | f | f
195 | CEE power plug | X700 | n/a | ylw/grn | 10 | 2010-1307 | X6 | 5.2 | Ground to main ground terminal |  | n/a | f | f
196 | 111600 | Q1 | X1 (profinet) | green | n/a | 6ES7214-1AG40-0XB0 | N1 | P2 | Profinet conn. switch and CPU |  | n/a | rj45 | rj45
197 | 111600 | Q1 | X2 (profinet) | green | n/a | Side panel connector | X631 | n/a | Profinett conn. to side panel |  | n/a | rj45 | rj45
198 | 111600 | Q1 | X3 (profinet) | n/a | n/a | free |  |  |  |  | n/a | n/a | n/a
199 | 111600 | Q1 | X4 (profinet) | green | n/a | Servo drive | N6 | X100 DQ | Profinet conn. to servo drive |  | n/a | rj45 | rj45
200 | 111600 | Q1 | X5 (profinet) | green | n/a | HMI | n/a | n/a | Profinet conn. to HMI |  | n/a | rj45 | rj45
201 | 111600 | Q1 | X6 (profinet) | n/a | n/a | Side panel connector | X741 | n/a | Profinett conn. to side panel |  | n/a | rj45 | rj45
202 | 111600 | Q1 | X7 (profinet) | n/a | n/a | Side panel connector | X742 | n/a | Profinett conn. to side panel |  | n/a | rj45 | rj45
203 | 111600 | Q1 | X8 (profinet) | n/a | n/a | Side panel connector | X720 | n/a | Profinet conn. to side panel |  | n/a | rj45 | rj45
204 | 2002-1401 | X3 | 8.1 | red | 0.75 | 1135752 | Q10 | IN+ 1.1 | +24V Rotary Airlock Valve |  | 300 | f | f
205 | 2002-1401 | X4 | 7.2 | black | 0.75 | 1135752 | Q10 | IN- 3.1 | 0V Rotary Airlock Valve |  | 300 | f | f
206 | 1135752 | Q10 | OUT+ 2.1 | red | 0.75 | 2900376 | K10 | 13 | +24V Rotary Airlock Valve |  | 1000 | f | f
207 | 2002-1401 | X4 | 7.4 | black | 0.75 | 2900376 | K10 | A2- | 0V Relais Rotary Airlock Valve |  | 1000 | f | f
208 | 2900376 | K10 | 14 | red | 0.75 | 890-703 | X760 | L | +24V Rotary Airlock Valve |  | 800 | f | n/a
209 | 2002-1401 | X4 | 7.5 | black | 0.75 | 890-703 | X760 | N | 0V Rotary Airlock Valve |  | 800 | f | n/a
210 | 2010-1307 | X2 | PE | ylw/grn | 0.75 | 890-703 | X760 | PE | PE Rotary Airlock Valve |  | 1000 | f | n/a
Note on J77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1a en 1b vervangen voor gewoon 1 tot 4

## BOM
|  |  | Name_list | Qnty_list | Component | qnty
301-2006 (900mm) | 0 | 0 | 301-2006 (900mm) | 1 | 301-2006 (900mm) | 1
758-9282 (160mm) | 0 | 0 | 758-9282 (160mm) | 1 | 758-9282 (160mm) | 1
758-9282 (450mm) | 0 | 0 | 758-9282 (450mm) | 3 | 758-9282 (450mm) | 3
758-9282 (450mm) | 0 | 0 | 758-9282 (250mm) | 2 | 758-9282 (250mm) | 2
758-9282 (450mm) | 0 | 0 | 0 | 0 | 742-4138 Din rail 430mm | 2
758-9282 (250mm) | 0 | 0 | 742-4138 Din rail 430mm | 2 | 249-116 | 14
758-9282 (250mm) | 0 | 0 | 249-116 | 14 | 6EP1433-2BA20 | 1
0 | 0 | 0 | 6EP1433-2BA20 | 1 | 6EP1961-2BA31 | 1
0 | 0 | 0 | 6EP1961-2BA31 | 1 | 2002-1401 | 15
742-4138 Din rail 430mm | 0 | 0 | 2002-1401 | 15 | 2002-1492 | 5
249-116 | 0 | 0 | 2002-1492 | 5 | 6ES7590-1AB60-0AA0 | 1
6EP1433-2BA20 | 0 | 0 | 1135752 | 1 | 6ES7511-1AK02-0AB0 | 1
6EP1961-2BA31 | 0 | 0 | 6ES7590-1AB60-0AA0 | 1 | 6ES7522-1BH01-0AB0 | 1
2002-1401 | 2002-402 (2P) | 0 | 6ES7511-1AK02-0AB0 | 1 | 6ES7521-1BH10-0AA0 | 1
2002-1401 | 0 | 0 | 6ES7522-1BH01-0AB0 | 1 | 3RV2021-4EA10 | 2
2002-1492 | 0 | 0 | 6ES7521-1BH10-0AA0 | 1 | 3RV2011-1DA10 | 1
2002-1401 | 2002-402 (2P) | 0 | 3RV2021-4EA10 | 2 | 5SY4103-7 | 1
2002-1401 | 0 | 0 | 3RV2021-1GA15 | 1 | 5SY4102-7 | 1
2002-1492 | 0 | 0 | 5SY4103-7 | 1 | 5SY4106-7 | 1
2002-1401 | 2002-402 (2P) | 0 | 5SY4102-7 | 1 | 5SY7463-7 | 1
2002-1401 | 0 | 0 | 5SY4106-7 | 1 | 2010-1201 | 11
2002-1492 | 0 | 0 | 5SY7463-7 | 1 | 2010-1292 | 6
2002-1401 | 2002-402 (2P) | 0 | 2010-1201 | 11 | 2010-1204 | 4
2002-1401 | 0 | 0 | 2010-1292 | 6 | 2010-1307 | 4
2002-1492 | 0 | 0 | 2010-1204 | 4 | 2010-1392 | 2
2002-1401 | 2002-404 (4P) | 0 | 2010-1307 | 4 | 742-4138 Din rail 250mm | 3
2002-1401 | 0 | 0 | 2010-1392 | 2 | 3RT2025-1BB40 | 1
2002-1401 | 0 | 0 | 742-4138 Din rail 250mm | 3 | 3RT2016-1BB41 | 1
2002-1401 | 0 | 2002-404 (4P) | 3RT2025-1BB40 | 1 | 111-3042 | 2
2002-1401 | 0 | 0 | 3RT2016-1BB41 | 1 | 5SY4306-7 | 1
2002-1401 | 0 | 0 | 111-3042 | 2 | 3RF2330-1AA02 | 5
2002-1401 | 0 | 0 | 5SY4306-7 | 1 | 2002-1204 | 5
2002-1492 | 0 | 0 | 2900376 | 1 | 2002-1292 | 1
1135752 | 0 | 0 | 3RF2330-1AA02 | 5 | 111600 | 1
249-116 | 0 | 0 | 2002-1204 | 5 | 6SL3203-0CE21-8AA0 | 1
0 | 0 | 0 | 2002-1292 | 1 | 6SL3210-1PE21-8AL0 | 1
0 | 0 | 0 | 111600 | 1 | 6SL3040-1LA01-0AA0 | 1
6ES7590-1AB60-0AA0 | Bridge | Bridge | Additional components mounted to the electrical plate | 1 | CQF12 + CK 03 IAN | 1
249-116 | 0 | 0 | 6SL3203-0CE23-8AA0 | 1 | CQF03 + CK 03 IAN | 1
6ES7511-1AK02-0AB0 | 0 | 0 | 6SL3210-1PE23-8AL0 | 1 | CQF05 + CK 03 IAN | 1
6ES7522-1BH01-0AB0 | 0 | 0 | 6SL3040-1LA01-0AA0 | 1 | 52015720 | 1
6ES7521-1BH10-0AA0 | 0 | 0 | Side panel 1 | 1 | E12408 | 3
249-116 | 0 | 0 | CQF12 + CK 03 IAN | 1 | 798-0704 | 2
0 | 0 | 0 | CQF03 + CK 03 IAN | 1 | 52115750 | 1
0 | 0 | 0 | CQF05 + CK 03 IAN | 1 | 2x IE100050 | 1
742-4138 Din rail 430mm | 0 | 0 | 52015720 | 1 | 1437779 | 1
249-116 | 0 | 0 | E12408 | 3 | 6SL3066-2DA00-0AA0 | 1
3RV2021-4EA10 | 0 | 0 | 798-0704 | 2 | 6FX2003-7BX00 | 1
3RV2021-1GA15 | 0 | 0 | Side panel 2 | 1 | RJ45 panel mount #1 | 1
5SY4103-7 | 0 | 0 | 52115750 | 1 | RJ45 panel mount #2 | 1
5SY4102-7 | 0 | 0 | 2x IE100050 | 1 | RJ45 panel mount #3 | 1
5SY4106-7 | 0 | 0 | 1437779 | 1 | IE100189 + IE100195 | 1
5SY7463-7 | 0 | 0 | 6SL3066-2DA00-0AA0 | 1 | Cabinet externals | 1
249-116 | 0 | 0 | 6FX2003-7BX00 | 1 | 285-507 | 2
2010-1201 | 2010-403 (3P) | 0 | RJ45 panel mount #1 | 1 | SK 3237.200 | 2
2010-1201 | 0 | 0 | RJ45 panel mount #2 | 1 | 3LD2203-0TK51 | 1
2010-1201 | 0 | 0 | RJ45 panel mount #3 | 1 | 3LD9200-5B | 1
2010-1292 | 0 | 0 | IE100189 + IE100195 | 1 | 6FX8002-5CN06-1AB0 | 1
2010-1201 | 2010-403 (3P) | 0 | 890-703 | 1 | 6FX8002-2DC00-1AB0 | 1
2010-1201 | 0 | 0 | Cabinet externals | 1 | 2002-402 (2P) | 4
2010-1201 | 0 | 0 | 285-507 | 2 | 2002-404 (4P) | 2
2010-1292 | 0 | 0 | SK 3237.200 | 2 | 2010-403 (3P) | 5
2010-1201 | 2010-402 (2P) | 0 | 3LD2504-0TK51 | 1 | 2010-402 (2P) | 1
2010-1201 | 0 | 0 | 3LD9200-5B | 1
2010-1292 | 0 | 0 | Cabinet servo and signal cables | 1
2010-1204 | 2010-403 (3P) | 0 | 6FX8002-5CN06-1AB0 | 1
2010-1204 | 0 | 0 | 6FX8002-2DC00-1AB0 | 1
2010-1204 | 0 | 0 | 0 | 0
2010-1292 | 0 | 0 | 2002-402 (2P) | 4
2010-1307 | 0 | 0 | 2002-404 (4P) | 2
2010-1307 | 0 | 0 | Bridge
2010-1307 | 0 | 0 | 2010-403 (3P)
2010-1392 | 0 | 0 | 2010-402 (2P)
249-116 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
742-4138 Din rail 250mm | 0 | 0
249-116 | 0 | 0
3RT2025-1BB40 | 0 | 0
3RT2016-1BB41 | 0 | 0
111-3042 | 0 | 0
111-3042 | 0 | 0
3RV2021-4EA10 | 0 | 0
5SY4306-7 | 0 | 0
2900376 | 0 | 0
249-116 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
742-4138 Din rail 250mm | 0 | 0
249-116 | 0 | 0
3RF2330-1AA02 | 0 | 0
3RF2330-1AA02 | 0 | 0
3RF2330-1AA02 | 0 | 0
3RF2330-1AA02 | 0 | 0
3RF2330-1AA02 | 0 | 0
249-116 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
742-4138 Din rail 250mm | 0 | 0
249-116 | 0 | 0
2010-1201 | 0 | 0
2010-1201 | 0 | 0
2010-1201 | 0 | 0
2010-1292 | 0 | 0
2010-1204 | 0 | 0
2010-1292 | 0 | 0
2010-1307 | 0 | 0
2010-1392 | 0 | 0
2002-1204 | 2010-403 (3P) | 0
2002-1204 | 0 | 0
2002-1204 | 0 | 2010-403 (3P)
2002-1204 | 0 | 0
2002-1204 | 0 | 0
2002-1292 | 0 | 0
249-116 | 0 | 0
111600 | 0 | 0
249-116 | 0 | 0
0 | 0 | 0
Additional components mounted to the electrical plate | 0 | 0
6SL3203-0CE23-8AA0 | 0 | 0
6SL3210-1PE23-8AL0 | 0 | 0
6SL3040-1LA01-0AA0 | 0 | 0
0 | 0 | 0
Side panel 1 | 0 | 0
CQF12 + CK 03 IAN | 0 | 0
CQF03 + CK 03 IAN | 0 | 0
CQF05 + CK 03 IAN | 0 | 0
52015720 | 0 | 0
E12408 | 0 | 0
E12408 | 0 | 0
E12408 | 0 | 0
798-0704 | 0 | 0
798-0704 | 0 | 0
0 | 0 | 0
0 | 0 | 0
Side panel 2 | 0 | 0
52115750 | 0 | 0
2x IE100050 | 0 | 0
1437779 | 0 | 0
6SL3066-2DA00-0AA0 | 0 | 0
6FX2003-7BX00 | 0 | 0
RJ45 panel mount #1 | 0 | 0
RJ45 panel mount #2 | 0 | 0
RJ45 panel mount #3 | 0 | 0
IE100189 + IE100195 | 0 | 0
890-703 | 0 | 0
0 | 0 | 0
Cabinet externals | 0 | 0
285-507 | 0 | 0
SK 3237.200 | 0 | 0
285-507 | 0 | 0
SK 3237.200 | 0 | 0
3LD2504-0TK51 | 0 | 0
3LD9200-5B | 0 | 0
0 | 0 | 0
Cabinet servo and signal cables | 0 | 0
6FX8002-5CN06-1AB0 | 0 | 0
6FX8002-2DC00-1AB0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0